## 1. Introduction
|  | Workbook Contents |  | Introduction to the MBBR worksheets in this workbook:
Click on tabs at the bottom of the screen to access the following: |  |  |  | Four worksheets are provided to carry out basin sizing and aeration calculations for the
following MBBR processes: 1. Single-Stage BOD Removal, 2. Two-Stage BOD Removal,
| Tab 1. Introduction (current tab) |  |  | 3. Two-stage BOD Removal and Nitrification, and 4. Single Stage Tertiary Nitrification.
In order to achieve an adequate nitrification rate in an MBBR reactor, the BOD level in
| Tab 2. Single-Stage BOD Removal |  |  | the wastewater entering the nitrification MBBR basin must be quite low. This is the
reason for carrying out BOD removal and nitrification in separate MBBR reactors.
Tab 3. Two-Stage BOD Removal
Basin sizing is based on a carrier surface area loading rate (SALR). For BOD removal, the
| Tab 4. Two-Stage BOD Removal and Nitrification |  |  | design SALR value is selected by the user based on the treatment objective (e.g. high rate
BOD removal, normal rate BOD removal, or low rate BOD removal. Typical SALR values
| Tab 5. Single-Stage Tertiary Nitrification |  |  | are provided on the worksheets. For nitrification, the design SALR is calculated from a
kinetic model based on the D.O. level to be maintained in the reactor and the target
| Tab 6. Derivation of Saturation DO vs T Equation |  |  | effluent ammonia nitrogen concentration.
Note that the estimated effluent BOD concentration from each BOD removal stage is
calculated by using an estimated value for the SARR/SALR (surface area removal rate/surface area
Why you shouldn’t give copies of this workbook away |  |  |  | loading rate). The estimated value for the SARR/SALR is based on an appropriate graph or table
We at EngineeringExcelTemplates.com hope that you find this workbook useful. If you |  |  |  | from one of the references as shown on the worksheets.
would like us to develop additional useful spreadsheets for you in the future, then encourage
your friends and colleagues to buy their own copies, rather than allowing them to copy |  |  |  | The basin sizing calculations require values for several MBBR carrier properties: (specific
the spreadsheet you purchased. We have deliberately set our prices so low that no one |  |  |  | surface area in m2/m3 and % void space). Values to be used in the design calculations
can really claim that they can’t afford to pay. But low prices will work for us—that is, we |  |  |  | should come from your carrier supplier.
can stay in business—only if we can sell enough copies. Bottom line: the more you get
other people to pay for their own copies, the more low-cost useful spreadsheets will be |  |  |  | The aeration/blower calculations are made for a coarse bubble diffuser system.
available for you in the future. |  |  |  | Coarse bubble diffusers are typically used, because they work better
with the suspended carrier media.
This workbook is provided "as is", without warranty of any kind, express or
implied.
Find more Excel spreadsheets for engineering at
EngineeringExcelTemplates.com
Copyright © 2017 Harlan H. Bengtson. All Rights Reserved.

## 2. Single-Stage-BOD Removal
MBBR Process Design Calculations - U.S. units
Single-Stage Process for BOD Removal
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
1. General Inputs
Data points for SARR/SALR vs SALR
Design ww Flow Rate, Q = |  | 0.02 | MGD |  | SALR (g/m2/d): |  | 7.5 | 25
Prim. Effl. BOD, So = |  | 200 | mg/L |  | SARR/SALR: |  | 0.925 | 0.775
Peak Hour Factor = |  | 4 |  | (default values above are based on the table of typical
|  |  |  | values of % BOD removal vs SALR at the right) | [5 empty] | Typical Design Values for Carrier Surface Area Loading Rate (SALR):
Design Value of BOD Surface |  |  |  |  | Slope, SARR/SALR vs SALR: |  |  | -0.0085714 |  | (from References (2) below)
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | Intercept, SARR/SALR vs SALR: |  |  | 0.98929
See information on typical design |  |  |  |  | Est. of SARR/SALR Ratio = |  |  | 0.93786
values for SALR below right. |  |  |  |  | (Surf. Area Removal Rate/Surf. Area Loading Rate)
(for SALR value specified at left)
2. Calculation of Carrier Volume and Required Tank Volume & Dimensions
Inputs |  |  |  |  | Liquid Depth in Tank = |  | 8 | ft
Carrier Spec. Surf. Area = |  | 396 | m2/m3 |  | Tank L:W ratio = |  | 1
(value from carrier mfr/vendor) |  |  |  | (target L:W - only used if tank is rectangular) | [5 empty] | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
Design Carrier Fill % = |  | 40% |  | Click on green box and then on | [5 empty] | equation are provided for each stage. They may be replaced by values from user data if such
(Carrier fill % is typically between 30% and |  |  |  | arrow to Select Tank Shape: |  |  | rectangular |  |  | data is available.
70%. Lower values are more conservative, |  |  |  |  | Carrier % Void Space = |  | 60%
allowing future capacity expansion or |  |  |  |  | (from carrier mfr/vendor - only needed to |  |  |  |  | Equations used for Tank Sizing
reduction of SALR by adding more carrier.) |  |  |  |  | calculate hydraulic detention time)
BOD Daily Loading = (Qo*So*8.34)
Calculations | [9 empty] | Carrier Surf. Area needed = BOD Daily Loading*453.59/SALR_BOD
BOD Daily Loading = |  | 33.36 | lb/day |  | Calculated Tank Volume = |  | 15.9215 | m3 |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
|  | 15131.7624 | g/day |  |  | = | 562.2613 | ft3 |  | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
[6 empty] | = | 4205.7146 | gal |  | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Carrier Surf. Area needed = |  | 2521.9604 | m2 | [6 empty] | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Calculated Carrier Volume = |  | 6.3686 | m3 |  | Calculated Tank Width = |  | 8.3835 | ft
[5 empty] | Calculated Tank Length = |  | 8.3835 | ft |  | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
Tank Liquid Volume = |  | 472.2995 | ft3 | Nominal Hydraulic Retention Time at | [5 empty] | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
[5 empty] | Design Average Flow = |  | 254.3616 | min |  | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Estimate of BOD Surface Area |  |  |  |  | Peak Hourly Flow = |  | 63.5904 | min |  | Estimated SARR = SALR(SARR/SALR)
Removal Rate, SARR = |  | 5.6271 | g/m2/d | [6 empty] | Estimated BOD Removal Rate = SARR*Carrier Surf Area
Est. of BOD Removal Rate: |  | 14191.4315 | g/day | Calculated Effl BOD Conc.: |  |  | 12.4286 | mg/L |  | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo/8.34
|  | 31.2869 | lb/day |  | If the calculated Effl. BOD conc. is too
[5 empty] | high, the design value of SALR |  |  |  | "Rules of Thumb" for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
[5 empty] | (in cell C13) should be reduced. |  |  |  | Source: Sanitaire, "Diffused Aeration Design Guide," available at:
3. Air Requirement | [8 empty] | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
Inputs: (Values of "Rule of Thumb" Constants for Calculations - see notes at right) | [9 empty] | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
(or 0.33 for a fine bubble aeration system)
O2 needed per lb BOD = |  | 1.5 | lb O2/lb BOD |  | Depth of Diffusers = |  | 7.5 | ft |  | 2. The typical SOTE is 0.75% per foot of diffuser submergence for a coarse bubble system
SOTE as Function of Depth = |  | 0.75% | % per ft depth |  | Standard Temperature = |  | 68 | oF |  |  | (or 2.0 % per foot of diffuser submergence for a fine bubble system)
AOTE/SOTE = |  | 0.5 |  |  | Standard Pressure = |  | 14.7 | psi |  | 3. I SCF of air weighs 0.075 lb/ft3 and contains 23% oxygen by weight, thus:
Press. Drop across Diffuser = |  | 12 | in W.C. |  | Atmospheric Pressure = |  | 14.7 | psi
(from mfr/vendor) |  |  |  |  | Air Density at STP = |  | 0.075 | lbm/SCF |  | 4. 1 SCF of air contains 0.0173 lbm of oxygen.
[5 empty] | O2 Content in Air = |  | 0.0173 | lbm/SCF
5. For biological treatment with SRT from 5 to 10 days, lb oxygen required /lb BOD removed
Calculations | [9 empty] | is typically in the range from 0.92 - 1.1 lb O2/lb BOD. Higher SRT results in a higher value
of lb O2 required/lb BOD removed. (For a very high SRT, as is typical for an MBBR process,
Oxygen Requirement = |  | 46.9304 | lb/day |  |  | AOTE = | 2.812% |  |  | this value would be about 1.5 lb O2/lb BOD removed.)
| SOTE = | 5.625% |  |  | Air Requirement = |  | 66.9812 | SCFM
Blower Outlet Pressure = |  | 18.3832 | psia | [6 empty] | 6. The oxidation of 1 lb of ammonia nitrogen typically requires 4.1 to 4.6 lb of oxygen.
References for additional background information:
1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
[10 empty] | Hong Kong, 12. 11-14-2014. |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
| Find more Excel spreadsheets for engineering at | [8 empty] | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
|  | EngineeringExcelTemplates.com | [7 empty] | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
| Copyright © 2017 Harlan H. Bengtson. All Rights Reserved. | [8 empty] | 3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
5. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
[10 empty] | 6. Bengtson, Harlan H., | Spreadsheets for MBBR Process Design Calculations,
available as a paperback book and as an Amazon Kindle ebook.
[10 empty] | 7. Bengtson, Harlan H., | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular

## 3. Two-Stage-BOD Removal
MBBR Process Design Calculations - U.S. units
Two-Stage Process for BOD Removal
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for Both First and Second Stage
Design ww Flow Rate, Q = |  | 0.02 | MGD |  | Peak Hour Factor = |  | 4
2. Parameters for First Stage: |  |  |  |  | Data points for SARR/SALR vs SALR |  |  |  | Typical Design Values for Carrier Surface Loading Rate (SALR):
[5 empty] | SALR (g/m2/d): |  | 7.5 | 25 | (from References (2) below)
Prim. Effl. BOD, So1 = |  | 200 | mg/L |  | SARR/SALR: |  | 0.925 | 0.775
(default values above are based on the table of typical
Design Value of BOD Surface |  |  |  | values of % BOD removal vs SALR at the right)
Area Loading Rate (SALR) = |  | 20 | g/m2/d |  | Slope, SARR/SALR vs SALR: |  |  | -0.0085714
See information on typical design |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.98929
values for SALR below right. |  |  |  |  | Est. of SARR/SALR Ratio = |  |  | 0.81786
(Surf. Area Removal Rate/Surf. Area Loading Rate)
3. Parameters for Second Stage:
Design Value of BOD Surface |  |  |  |  | Est. of SARR/SALR Ratio = |  | 0.94643 |  | Estimation of SARR/SALR Ratio: Default data points for derivation of a SARR vs SALR
Area Loading Rate (SALR) = |  | 5 | g/m2/d |  | (Surf. Area Removal Rate/Surf. Area Loading Rate) |  |  |  | equation are provided for each stage. They may be replaced by values from user data if such
See information on typical design | [8 empty] | data is available.
values for SALR to the right.
II. Carrier Parameter and Tank Shape Inputs for both First and Second Stages
Carrier Spec. Surf. Area = |  | 396 | m2/m3 | Click on green box and then on
(value from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
Liquid Depth in Tank = |  | 8 | ft |  | Carrier % Void Space = |  | 60%
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time)
III. Calculation of Carrier Volume and Required Tank Volume & Dimensions | [8 empty] | Equations used for Tank Sizing (First Stage BOD Removal)
1. First Stage Calculations (BOD Removal) |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower |  |  |  | BOD Daily Loading = (Qo*So*8.34)
[5 empty] | values are more conservative, allowing future capacity |  |  |  | Carrier Surf. Area needed = BOD Daily Loading*453.59/SALR_BOD
Design Carrier Fill % = |  | 50% | (for first stage) |  | expansion or reduction of SALR by adding more carrier. |  |  |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
BOD Daily Loading = |  | 33.36 | lb/day | [5 empty] | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
|  | 15131.7624 | g/day |  | Calculated Tank Volume = |  | 3.8212 | m3 | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Carrier Surf. Area needed = |  | 756.5881 | m2 |  |  | = | 134.9427 | ft3 | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Calculated Carrier Volume = |  | 1.9106 | m3 |  |  | = | 1009.3715 | gal
Tank Liquid Volume = |  | 107.9542 | ft3 |  | Calculated Tank Width = |  | 3.3534 | ft | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
[5 empty] | Calculated Tank Length = |  | 5.0301 | ft | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
Estimate of BOD Surface Area |  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Removal Rate, SARR = |  | 16.3571 | g/m2/d |  | Design Average Flow = |  | 58.1398 | min | Estimated SARR = SALR(SARR/SALR)
Est. of BOD Removal Rate: |  | 12375.62 | g/day |  | Peak Hourly Flow = |  | 14.5349 | min | Estimated BOD Removal Rate = SARR*Carrier Surf Area
|  | 27.2837 | lb/day |  | Calculated Effl BOD Conc.: |  | 36.4286 | mg/L | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo/8.34
(from First Stage)
2. Second Stage Calculations (BOD Removal)
Equations used for Tank Sizing (Second Stage BOD Removal)
Design Carrier Fill % = |  | 36.43% | (for second stage)
BOD Daily Loading = |  | 6.0763 | lb/day |  | Calculated Tank Volume = |  | 3.8212 | m3 | The equations used are the same as those shown above for the First Stage BOD Removal,
|  | 2756.1424 | g/day |  |  | = | 134.945 | ft3 | Removal, except that the value for So used to calculate the BOD Daily Loading is the
Carrier Surf. Area needed = |  | 551.2285 | m2 |  |  | = | 1009.389 | gal | Effluent BOD concentration from the First Stage.
Calculated Carrier Volume = |  | 1.392 | m3 |  | Calculated Tank Width = |  | 3.3534 | ft
Tank Liquid Volume = |  | 115.282 | ft3 |  | Calculated Tank Length = |  | 5.0301 | ft
Nominal Hydraulic Retention Time at
Estimate of BOD Surface Area |  |  |  |  | Design Average Flow = |  | 62.0863 | min | Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
Removal Rate, SARR = |  | 4.7321 | g/m2/d |  | Peak Hourly Flow = |  | 15.5216 | min | Source:
Est. of BOD Removal Rate: |  | 2608.4919 | g/day |  | Calculated Effl BOD Conc.: |  | 1.9515 | mg/L | http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
|  | 5.7508 | lb/day |  | (from Second Stage)
1st stage tank volume - |  |  |  | If the calculated Effl. BOD conc. is too high for either |  |  |  |  | 1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
- 2nd stage tank volume = |  | -6.6152e-05 |  | stage, the design value of SALR should be reduced | [6 empty] | (or 0.33 for a fine bubble aeration system)
To make the 2nd stage tank volume the same as the first | [6 empty] | for that stage. |  | 2. The typical SOTE is 0.75% per foot of diffuser submergence for a coarse bubble system
stage tank volume, use Excel's Goal Seek process to set | [9 empty] | (or 2.0 % per foot of diffuser submergence for a fine bubble system)
cell C66 equal to zero by changing the value in cell C54. | [8 empty] | 3. I SCF of air weighs 0.075 lb/ft3 and contains 23% oxygen by weight, thus:
IV. Calculation of Oxygen/Air/Blower Requirements
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right) | [8 empty] | 4. 1 SCF of air contains 0.0173 lbm of oxygen.
O2 needed per lb BOD = |  | 1.5 | lb O2/lb BOD |  | Depth of Diffusers = |  | 7.5 | ft | 5. For biological treatment with SRT from 5 to 10 days, lb oxygen required /lb BOD removed
SOTE as Function of Depth = |  | 0.75% | % per ft depth |  | Standard Temperature = |  | 68 | oF | is typically in the range from 0.92 - 1.1 lb O2/lb BOD. Higher SRT results in a higher value
AOTE/SOTE = |  | 0.5 |  |  | Standard Pressure = |  | 14.7 | psi | of lb O2 required/lb BOD removed. (For a very high SRT, as is typical for an MBBR process,
Press. Drop across Diffuser = |  | 12 | in W.C. |  | Atmospheric Pressure = |  | 14.7 | psi | this value would be about 1.5 lb O2/lb BOD removed.)
(from mfr/vendor) |  |  |  |  | Air Density at STP = |  | 0.075 | lbm/SCF
[5 empty] | O2 Content in Air = |  | 0.0173 | lbm/SCF | 6. The oxidation of 1 lb of ammonia nitrogen typically requires 4.1 to 4.6 lb of oxygen.
2. First Stage Calculations:
Oxygen Requirement = |  | 40.9256 | lb/day |  |  | AOTE = | 2.812% |  | References for additional background information:
| SOTE = | 5.625% |  |  | Air Requirement = |  | 58.4109 | SCFM
Blower Outlet Pressure = |  | 18.3832 | psia | [5 empty] | 1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
[9 empty] | Hong Kong, 12. 11-14-2014. |  | http://www.dsd.gov.hk/rdforum/2014/ppt/Presentation_(B4-1).pdf
3. Second Stage Calculations:
2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
Oxygen Requirement = |  | 8.6262 | lb/day |  |  | AOTE = | 2.812% |  | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
| SOTE = | 5.625% |  |  | Air Requirement = |  | 12.3116 | SCFM | http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
Blower Outlet Pressure = |  | 18.3832 | psia
3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Find more Excel spreadsheets for engineering at
|  | EngineeringExcelTemplates.com | [6 empty] | 4. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
| Copyright © 2017 Harlan H. Bengtson. All Rights Reserved. | [7 empty] | 5. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
[9 empty] | 6. Bengtson, Harlan H., | Spreadsheets for MBBR Process Design Calculations,
available as a paperback book and as an Amazon Kindle ebook.
[9 empty] | 7. Bengtson, Harlan H., | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular

## 4. Two-Stage-BOD Rem.-Nitrif.
MBBR Process Design Calculations - U.S. units
Two-Stage Process for BOD Removal & Nitrification
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
I. Wastewater Parameter Inputs
1. Parameters for Both First and Second Stage
Design ww Flow Rate, Q = |  | 0.2 | MGD |  | Peak Hour Factor = |  | 4
|  |  | Prim. Effl. Alkalinity = |  |  | 140 | mg/L as CaCO3
2. Parameters for First Stage: |  |  |  |  | Data points for SARR/SALR vs SALR |  |  |  | Typical Design Values for Carrier Surface Loading Rate (SALR):
[5 empty] | SALR (g/m2/d): |  | 7.5 | 15 | (from References (2) below)
Prim. Effl. BOD, So1 = |  | 180 | mg/L |  | SARR/SALR: |  | 0.925 | 0.875 | [5 empty] | Nitrification SARR:
(default values above are based on the table of typical
Design Value of BOD Surface |  |  |  | values of % BOD removal vs SALR in Worksheet 3)
Area Loading Rate (SALR) = |  | 6 | g/m2/d |  | Slope, SARR/SALR vs SALR: |  |  | -0.0066667
See information on typical design |  |  |  |  | Intercept, SARR/SALR vs SALR: |  |  | 0.975
values for SALR at the right. |  |  |  |  | Est. of SARR/SALR Ratio = |  |  | 0.935
(Surf. Area Removal Rate/Surf. Area Loading Rate)
3. Parameters for Second Stage:
Influent NH4-N Conc. = |  | 25 | mg/L | Target Effl NH4-N Conc, NH4-Ne = |  |  | 3.3 | mg/L | Estimation of SARR/SALR Ratio: Default data points for derivation
Min Design Temp., T = |  | 45 | oF | Click on cell H26 and on arrow to select D.O Conc. |  |  |  |  | of a SARR vs SALR equation are provided for the BOD stage. They may
[5 empty] | D.O Conc. in Reactor = |  | 3 | mg/L | be replaced by values from user data if such data is available.
4. Preliminary Calculations - Design Nitrification SALR value | [13 empty] | Adapted from Metcalf & Eddy, 5th Ed, Fig 9-25
Nitrification SARR:
% NH4-N removal = |  | 86.8% |  |  | NH4-Ne @ SARRmax = |  | 0.8 | mg/L | D.O. | SARRmax | N @ SARRmax |  | The values in the table at the left come from Figure 9-25 in Metcalf & Eddy,
Maximum SARR = |  | 0.88 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.88 | g/m2/d | mg/L | g/m2/d | mg/L |  | Wastewater Engineering, Treatment and Resource Recovery, 5th Ed.
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.5676 | g/m2/d | 2 | 0.61 | 0.5 |  | The N values at SARRmax were read from Figure 9-25. The SARRmax
SARR Temp. Coeff, q = |  | 1.058 | Design Value for nitrification SALR = |  |  |  | 0.65391 | g/m2/d | 3 | 0.88 | 0.8 |  | values were calculated for those N values using Eqn 9-48 from Metcalf & Eddy,
II. Carrier Parameter and Tank Shape Inputs for both First and Second Stages | [8 empty] | 4 | 1.03 | 1 |  | 5th Ed: SARR = [N/(2.2 + N)]*3.3, where N is the bulk liquid (effluent)
[9 empty] | 5 | 1.23 | 1.3 |  | NH4-N concentration.
Carrier Spec. Surf. Area = |  | 600 | m2/m3 | Click on green box and then on |  |  |  |  | 6 | 1.41 | 1.65 |  | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
(value from carrier mfr/vendor) |  |  |  | arrow to Select Tank Shape: |  |  | rectangular | [5 empty] | conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
Liquid Depth in Tank = |  | 8 | ft |  | Carrier % Void Space = |  | 60% |  | 3 | 0.88 | 0.8 |  | SARR temperature adjustments are made with: |  | SARRT = SARR15q(T - 15)
Tank L:W ratio = |  | 1.5 |  |  | (from carrier mfr/vendor - only needed to
(target L:W - only used if tank is rectangular) |  |  |  |  | calculate hydraulic detention time) | [7 empty] | SALR is calculated as SARR/% removal.
III. Calculation of Carrier Volume and Required Tank Volume & Dimensions | [8 empty] | Equations used for Tank Sizing (BOD Removal Stage)
1. First Stage Calculations - BOD Removal |  |  |  |  | (Carrier fill % is typically between 30% and 70%. Lower |  |  |  | BOD Daily Loading = (Qo*So*8.34)
[5 empty] | values are more conservative, allowing future capacity |  |  |  | Carrier Surf. Area needed = BOD Daily Loading*453.59/SALR_BOD
Design Carrier Fill % = |  | 40% | (for first stage) |  | expansion or reduction of SALR by adding more carrier. |  |  |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
BOD Daily Loading = |  | 300.24 | lb/day | [5 empty] | Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
|  | 136185.8616 | g/day |  | Calculated Tank Volume = |  | 94.5735 | m3 | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
Carrier Surf. Area needed = |  | 22697.6436 | m2 |  |  | = | 3339.8322 | ft3 | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
Calculated Carrier Volume = |  | 37.8294 | m3 |  |  | = | 24981.9446 | gal
Tank Liquid Volume = |  | 2805.459 | ft3 |  | Calculated Tank Width = |  | 16.6829 | ft | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
|  | 1335.8841 | 3339.7103 |  | Calculated Tank Length = |  | 25.0244 | ft | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
Estimate of BOD Surface Area |  |  |  | Nominal Hydraulic Retention Time at |  |  |  |  | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Removal Rate, SARR = |  | 5.61 | g/m2/d |  | Design Average Flow = |  | 151.0908 | min | Estimated SARR = SALR(SARR/SALR)
Est. of BOD Removal Rate: |  | 127333.7806 | g/day |  | Peak Hourly Flow = |  | 37.7727 | min | Estimated BOD Removal Rate = SARR*Carrier Surf Area
|  | 280.7244 | lb/day |  | Calculated Effl BOD Conc.: |  | 11.7 | mg/L | Calculated Eff. BOD Conc. = (BOD Daily Loading - BOD Removal Rate)/Qo/8.34
(from First Stage)
If the calculated Effl. BOD conc. is too high, the design value of the SALR should be reduced in cell C18.
2. Second Stage Calculations - Nitrification
[5 empty] | Calculated Tank Volume = |  | 120.5229 | m3 | Equations used for Tank Sizing - Nitrification Stage
Design Carrier Fill % = |  | 40% | (for second stage) |  |  | = | 4256.2245 | ft3
NH3-N Daily Loading = |  | 41.7 | lb/day |  |  | = | 31836.5596 | gal | NH3-N Daily Loading = Qo*Prim Effl NH3-N*8.34
|  | 18914.703 | g/day |  | Calculated Tank Width = |  | 18.8331 | ft | Carrier Surf. Area needed = NH3-N Daily Loading*453.59/SALR_NH3-N
Carrier Surf. Area needed = |  | 28925.4858 | m2 |  | Calculated Tank Length = |  | 28.2496 | ft | Carrier Volume needed, Required Tank Volume, and Tank dimensions
Calculated Carrier Volume = |  | 48.2091 | m3 | Nominal Hydraulic Retention Time at |  |  |  |  | use the same equations shown above.
Tank Liquid Volume = |  | 3721.8514 | ft3 |  | Design Average Flow = |  | 200.444 | min
1st stage tank volume - |  | 1702.4277 | 4256.0693 |  | Peak Hourly Flow = |  | 50.111 | min | Tank Liquid Volume, Nominal HRTs, and Estimated SARR are
- 2nd stage tank volume = |  | -25.9493 | [6 empty] | calculated as shown above.
To make the 2nd stage tank volume the same as the |  |  |  |  | Check on BOD SALR: |  | 0.30603 | g/m2/d | Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
first stage, use Excel's Goal Seek process to set cell |  |  |  |  | (BOD SALR should be < 0.5 g/m2/d in order |  |  |  | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo/8.34
C71 equal to zero by changing the value in cell C60. |  |  |  |  | to achieve a good nitrification rate)
Rules of Thumb for Estimating Oxygen/Air Requirements - Coarse Bubble Diffusers:
IV. Calculation of Oxygen/Air/Blower Requirements - BOD Removal Stage | [8 empty] | Source:
http://www.xylemwatersolutions.com/scs/sweden/sv-se/produkter/cirkulationspumpar/documents/san3.pdf
1. Inputs: (Values of "Rule of Thumb" Constants to be used in Calculations - See notes at right)
1. The typical AOR/SOR (or AOTE/SOTE) is 0.50 for a coarse bubble aertion system.
O2 needed per lb BOD = |  | 1.5 | lb O2/lb BOD |  | Depth of Diffusers = |  | 7.5 | ft |  |  |  | (or 0.33 for a fine bubble aeration system)
SOTE as Function of Depth = |  | 0.75% | % per ft depth |  | Standard Temperature = |  | 68 | oF | 2. The typical SOTE is 0.75% per foot of diffuser submergence for a coarse bubble system
AOTE/SOTE = |  | 0.5 |  |  | Standard Pressure = |  | 14.7 | psi |  |  | (or 2.0 % per foot of diffuser submergence for a fine bubble system)
Press. Drop across Diffuser = |  | 12 | in W.C. |  | Atmospheric Pressure = |  | 14.7 | psi | 3. 1 SCF of air weighs 0.075 lb/ft3 and contains 23% oxygen by weight, thus:
(from mfr/vendor) |  |  |  |  | Air Density at STP = |  | 0.075 | lbm/SCF
[5 empty] | O2 Content in Air = |  | 0.0173 | lbm/SCF | 4. 1 SCF of air contains 0.0173 lbm of oxygen.
Calculations
5. For biological treatment with SRT from 5 to 10 days, lb oxygen required /lb BOD removed
Oxygen Requirement = |  | 421.0866 | lb/day |  |  | AOTE = | 2.812% |  | is typically in the range from 0.92 - 1.1 lb O2/lb BOD. Higher SRT results in a higher value
| SOTE = | 5.625% |  |  | Air Requirement = |  | 600.9942 | SCFM | of lb O2 required/lb BOD removed. (For a very high SRT, as is typical for an MBBR process,
Blower Outlet Pressure = |  | 18.3832 | psia | [5 empty] | this value would be about 1.5 lb O2/lb BOD removed.)
V. Calculation of Oxygen/Air/Blower Requirements - Nitrification Stage | [8 empty] | 6. The oxidation of 1 lb of ammonia nitrogen typically requires 4.1 to 4.6 lb of oxygen.
Inputs:
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 14.5 | psi | Equations used for Oxygen/Air/Blower Calculations
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site)
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean |  |  |  | Oxygen Requirement (lb/day) = Qo(4.57(NH4-No - NH4-Ne)*[(mg/L)/(lb/MG)]
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across |  |  |  | Pressure at Mid-Depth = Patm + [g4H2O(ddiff/2)]/144 in2/ft2
Depth of diffuser, ddiff = |  | 7.5 | ft |  | diffuser, DPdiff = |  | 12 | in H2O
Std. Air Density, rair = |  | 0.07521 | lb/ft3 |  | (from diffuser mfr or vendor) |  |  |  | AOTE = SOTE*a*F[(B(PD/Pstd)Cs - D.O.)/Css]q(tww - 20)
SCFM = (lb/day O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(60 min/hr)(24 hr/day)]
Calculations
ACFM = SCFM[(Tww + 459.67)/(Tstd + 459.67)](Pstd/PB2)
Oxygen Requirement = |  | 165.4139 | lb/day |  | Act O2 transf effic, AOTE = |  | 2.218%
Pressure at mid Depth, PD = |  | 16.125 | psi |  | Des. Air Flow Rate, SCFM = |  | 298.2209 | SCFM | PB2 = Patm + DPdiff(0.036126 psi/in H2O) + gH2O*ddiff/144 in2/ft2
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, ACFM = |  | 230.5806 | ACFM
temp. and 1 atm, Cs = |  | 12.0764 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 18.1835 | psi
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 6) | [8 empty] | References for additional background information:
V. Calculation of Alkalinity Requirements | [8 empty] | 1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
[9 empty] | Hong Kong, 12. 11-14-2014. |  |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L
2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
Constants needed for Calculations: | [8 empty] | Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv.
3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N |  |  |  |  | IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Calculations
4. Rusten, B and Paulrud, B., Improved nutrient Removal with Biofilm Reactors,
Alkalinity to be added = |  |  | 94.938 | mg/L as CaCO3 |  |  |  |  | Aquateam - Norwegian Water Technology Center, Oslo, Norway.
Daily Alkalinity Requirement = |  |  | 158.3566 | lb/day as CaCO3
5. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
For sodium bicarbonate use to add alkalinity: | [8 empty] | Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
Daily NaHCO3 Requirement = |  |  | 266.0391 | lb/day NaHCO3 |  |  |  |  | 6. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
7. Salvetti, R., A. Azzellino, R. Canziani, and L. Bonomo (2006), "Effect of Temperature on Tertiary
Nitrification in Moving-Bed Biofilm Reactors," Water Res., 40, 15, 298-2993.
Find more Excel spreadsheets for engineering at
|  | EngineeringExcelTemplates.com | [6 empty] | 8. Bengtson, Harlan H., |  | Spreadsheets for MBBR Process Design Calculations,
available as a paperback book and as an Amazon Kindle ebook.
| Copyright © 2017 Harlan H. Bengtson. All Rights Reserved. | [7 empty] | 9. Bengtson, Harlan H., |  | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular
2
3
4
5
6

## 5. Single-Stage Tertiary Nitrif
MBBR Process Design Calculations - U.S. units
Single Stage Tertiary Nitrification Process
Instructions: Enter values in blue boxes. Spreadsheet calculates values in yellow boxes
1. General Inputs |  |  |  |  | Peak Hour Factor = |  | 4
|  |  |  | Target Effl NH4-N Conc, NH4-Ne = |  |  | 3.3 | mg/L
Design ww Flow Rate, Q = |  | 0.2 | MGD |  | Min Design Temp., T = |  | 50 | oF
Influent NH4-N Conc. = |  | 25 | mg/L
Influent BOD, So = |  | 15 | mg/L |  | Click on cell H10 and on arrow to select D.O Conc.
Prim. Effl. Alkalinity = |  | 140 | mg/L as CaCO3 |  | D.O Conc. in Reactor = |  | 3 | mg/L
Adapted from Metcalf & Eddy, 5th Ed, Fig 9-25
2. Preliminary Calculations - Design SALR value | [8 empty] | D.O. | SARRmax | N @ SARRmax | The values in the table at the left come from Figure 9-25 in Metcalf & Eddy,
[9 empty] | mg/L | g/m2/d | mg/L | Wastewater Engineering, Treatment and Resource Recovery, 5th Ed.
% NH4-N removal = |  | 86.8% |  |  | NH4-Ne @ SARRmax = |  | 0.8 | mg/L | 2 | 0.61 | 0.5 | The N values at SARRmax were read from Figure 9-25. The SARRmax
Maximum SARR = |  | 0.88 | g/m2/d | SARR @ NH4-Ne, 15oC, SARR15 = |  |  | 0.88 | g/m2/d | 3 | 0.88 | 0.8 | values were calculated for those N values using Eqn 9-48 from Metcalf & Eddy,
|  |  |  | SARR @ NH4-Ne, T oC, SARRT = |  |  | 0.66383 | g/m2/d | 4 | 1.03 | 1 | 5th Ed: SARR = [N/(2.2 + N)]*3.3, where N is the bulk liquid (effluent)
SARR Temp. Coeff, q = |  | 1.058 | [6 empty] | 5 | 1.23 | 1.3 | NH4-N concentration.
[5 empty] | Design Value for SALR = |  | 0.76478 | g/m2/d | 6 | 1.41 | 1.65 | SARR temperature correction coefficients being used are: q = 1.058 for DO limited
conditions and q = 1.098 for ammonia limited conditions. (per Salvetti et al - see ref list below)
3. Calculation of Carrier Volume and Required Tank Volume & Dimensions | [8 empty] | 3 | 0.88 | 0.8 | SARR temperature adjustments are made with: |  |  | SARRT = SARR15q(T - 15)
Inputs | [11 empty] | SALR is calculated as SARR/% removal.
Carrier Spec. Surf. Area = |  | 600 | m2/m3 |  | Liquid Depth in Tank = |  | 8 | ft
(value from carrier mfr/vendor) |  |  |  |  | Tank L:W ratio = |  | 1.5
(target L:W - only used if tank is rectangular)
Design Carrier Fill % = |  | 40% |  | Click on green box and then on |  |  |  |  | Equations used for Tank Sizing
(Carrier fill % is typically between 30% and |  |  |  | arrow to Select Tank Shape: |  |  | rectangular
70%. Lower values are more conservative, |  |  |  |  | Carrier % Void Space = |  | 60% |  | NH3-N Daily Loading = Qo*Prim Effl NH3-N*8.34
allowing future capacity expansion or |  |  |  |  | (from carrier mfr/vendor - only needed to |  |  |  | Carrier Surf. Area needed = NH3-N Daily Loading*453.59/SALR_NH3-N
reduction of SALR by adding more carrier.) |  |  |  |  | calculate hydraulic detention time) |  |  |  | Carrier Volume needed = Carrier Surf Area/Carrier Spec Surf Area
Required Tank Volume = Carrier Volume/Des Carrier Fill PerCent
Calculations | [8 empty] | Tank Width & Length calculated from: Tank Volume = L*W*Liquid Depth
[5 empty] | Calculated Tank Volume = |  | 103.0513 | m3 | Or, Tank Diameter calculated from: Tank Volume = (pD2/4)Liquid Depth
NH3-N Daily Loading = |  | 41.7 | lb/day |  |  | = | 3639.224 | ft3
|  | 18914.703 | g/day |  |  | = | 27221.3955 | gal | Tank Liquid Volume = Tank Volume-((1-Carrier PerCent Void)*Carrier Volume)
Carrier Surf. Area needed = |  | 24732.3235 | m2 |  | Calculated Tank Width = |  | 17.4146 | ft | Nominal HRT at Des Ave Flow = Tank Liq Vol/(WW Flow Rate/(24*60))
Calculated Carrier Volume = |  | 41.2205 | m3 |  | Calculated Tank Length = |  | 26.1219 | ft | Nominal HRT at Peak Hourly Flow = Hydr Det Time at Des Ave Flow/Peak Hour Factor
Tank Liquid Volume = |  | 3056.9482 | ft3 | Nominal Hydraulic Retention Time at |  |  |  |  | Estimated SARR = SALR(SARR/SALR)
[5 empty] | Design Average Flow = |  | 164.635 | min | Estimated NH3-N Removal Rate = SARR*Carrier Surf Area
BOD Surf. Loading Rate (SALR): |  |  | 0.45887 | g/m2/d Peak Hourly Flow = |  |  | 41.1588 | min | Calculated Eff. NH3-N Conc. = (NH3-N Daily Loading - NH3-N Removal Rate)/Qo/8.34
(should be < 0.5 g/m2/d in order to achieve a good nitrification rate)
4. Calculation of Oxygen/Air/Blower Requirements
Inputs: | [8 empty] | Equations used for Oxygen/Air/Blower Calculations
Std O2 transf effic, SOTE = |  | 5.6% |  |  | Des. Barom. Press., Patm = |  | 14.7 | psi | Oxygen Requirement (lb/day) = Qo(4.57(NH4-No - NH4-Ne)*[(mg/L)/(lb/MG)]
(from diffuser mfr or vendor) |  |  |  |  | (ambient pressue at site)
Diffuser Fouling Factor, F = |  | 0.8 |  |  | Ratio of D.O. saturation in WW to that in clean |  |  |  | Pressure at Mid-Depth = Patm + [g4H2O(ddiff/2)]/144 in2/ft2
Ratio of oxygen transfer rate in wastewater |  |  |  |  | water at same T & P, B = |  | 1
to that in clean water, a = |  | 0.6 |  |  | Pressure drop across |  |  |  | AOTE = SOTE*a*F[(B(PD/Pstd)Cs - D.O.)/Css]q(tww - 20) |  |  |  | (Tww in oC)
Depth of diffuser, ddiff = |  | 7.5 | ft |  | diffuser, DPdiff = |  | 12 | in H2O
Std. Air Density, rair = |  | 0.07521 | lb/ft3 |  | (from diffuser mfr or vendor) |  |  |  | SCFM = (lb/day O2/AOTE)*MWair/[O2 fract in air)(MWO2)(rair)(60 min/hr)(24 hr/day)]
Calculations
ACFM = SCFM[(Tww + 459.67)/(Tstd + 459.67)](Pstd/PB2)
Oxygen Requirement = |  | 165.4139 | lb/day |  | Act O2 transf effic, AOTE = |  | 2.205%
Pressure at mid Depth, PD = |  | 16.325 | psi |  | Des. Air Flow Rate, SCFM = |  | 300.0058 | SCFM | PB2 = Patm + DPdiff(0.036126 psi/in H2O) + gH2O*ddiff/144 in2/ft2
D.O sat'n conc. for clean water at ww |  |  |  |  | Des. Air Flow Rate, ACFM = |  | 231.7102 | ACFM
temp. and 1 atm, Cs = |  | 11.2888 | mg/L | Blower Outlet Pressure, PB2 = |  |  | 18.3835 | psi
(Derivation of equation for sat'n D.O. vs T is shown on worksheet 6)
References for additional background information:
5. Alkalinity Requirement
1. Odegaard, Hallvard, "Compact Wastewater Treatment with MBBR." DSD International Conference
Input: | Target Effluent Alkalinity = |  |  |  | 80 | mg/L |  |  | Hong Kong, 12. 11-14-2014. |  |  | http://www.dsdic2014.hk/ppt/Presentation_(B4-1).pdf
Constants needed for Calculations: | [8 empty] | 2. Odegaard, H., "The Moving Bed Biofilm Reactor," in Igasrashi, T, Watanabe, Y., Asano, T. and
Tambo, N., Water Environmental Engineering and Reuse of Water, Hokkaido Press 1999, p 250-305.
Equiv Wt. of CaCO3 = |  | 50 | g/equiv. |  | Equiv Wt. of NaHCO3 = |  | 84 | g/equiv. | http://netedu.xauat.edu.cn/jpkc/netedu/jpkc2009/szylyybh/content/wlzy/7/3/The%20Moving%20Bed%20Biofilm%20Reactor.pdf
Alkalinity used for Nitrification = |  |  | 7.14 | g CaCO3/g NH3-N |  |  |  |  | 3. Steichen & Phillips, H., M, Black & Veach, Process and Practical Design Considerations for
IFAS and MBBR Technologies, Headworks International Presentation, 03/18/2010
Calculations | [8 empty] | http://www.headworksinternational.com/userfiles/file/Webinar/BV_Webinar_Slides.pdf
Alkalinity to be added = |  |  | 118.5 | mg/L as CaCO3 |  |  |  |  | 4. Rusten, B and Paulrud, B., Improved nutrient Removal with Biofilm Reactors,
Daily Alkalinity Requirement = |  |  | 197.658 | lb/day as CaCO3 |  |  |  |  | Aquateam - Norwegian Water Technology Center, Oslo, Norway.
For sodium bicarbonate use to add alkalinity: | [8 empty] | 5. McQuarrie, J.P. and Boltz, J.P., Moving Bed Biofilm Reactor Technology: Process Applications,
Design and Performance, Water Environment Research, Vol 83, No. 6. June 2011.
Daily NaHCO3 Requirement = |  |  | 332.0654 | lb/day NaHCO3
6. Metcalf & Eddy, "Wastewater Engineering Treatment and Resource Recovery", 5th Ed, McGraw-Hill, 2014
7. Salvetti, R., A. Azzellino, R. Canziani, and L. Bonomo (2006), "Effect of Temperature on Tertiary
| Find more Excel spreadsheets for engineering at | [7 empty] | Nitrification in Moving-Bed Biofilm Reactors," Water Res., 40, 15, 298-2993.
EngineeringExcelTemplates.com
[9 empty] | 8. Bengtson, Harlan H., |  | Spreadsheets for MBBR Process Design Calculations,
available as a paperback book and as an Amazon Kindle ebook.
Copyright © 2017 Harlan H. Bengtson. All Rights Reserved.
[9 empty] | 9. Bengtson, Harlan H., |  | Biological Wastewater Treatment Process Design Calculations
available as a paperback book and as an Amazon Kindle ebook.
cylindrical
rectangular
2
3
4
5
6

## 6. Satn DO vs T
Derivation of Equation for Saturation DO Concentration at WW Temperature:
Sat'n DO
T, oF | mg/L
35 | 13.96
36 | 13.75
37 | 13.54
38 | 13.34
39 | 13.15
40 | 12.96
41 | 12.77
42 | 12.59
43 | 12.41
44 | 12.24
45 | 12.07
46 | 11.91
47 | 11.75
48 | 11.59
49 | 11.44
50 | 11.29
51 | 11.14
52 | 11 | Source for DO vs T data: USGS website at:
53 | 10.86
54 | 10.72 |  | http://water.usgs.gov/software/DOTABLES/
55 | 10.59
56 | 10.46
57 | 10.33
58 | 10.21
59 | 10.08
60 | 9.96
61 | 9.85
62 | 9.73
63 | 9.62
64 | 9.51
65 | 9.4
66 | 9.3
67 | 9.19
68 | 9.09
69 | 8.99
70 | 8.9
71 | 8.8
72 | 8.71
73 | 8.61
74 | 8.52
75 | 8.44
76 | 8.35
77 | 8.26
78 | 8.18
79 | 8.1
80 | 8.02

## Sheet1
min NH3-Ne
D.O. | SARRmax | @ SARRmax
mg/L | g/m2/d | mg/L
2 | 0.61 | 0.5
3 | 0.88 | 0.8
4 | 1.03 | 1
5 | 1.23 | 1.3
6 | 1.41 | 1.65